## LCAC_Cassettes_EN
EN |  |  |  |  | MODEL NAMES
[5 empty] | V6MCRI32-18WiFiR/U6MRS32-18 | V5MCI32-24WiFiR/U5MRS32-24 | V5MCI32-36WiFiR/U5MRS32-36 | V5MCI32-50WiFiR/U5MRT32-50 | V5MCI32-60WiFiR/U5MRT32-60
SPECIFICATIONS |  | Cooling Capacity (Btu/h) |  |  | 18.000 (9.900-19.600) | 24.000 (10.990-28.000) | 36.000 (13.800-41.000) | 48.000 (16.224-49.761) | 53.000 (18.000-57.000)
|  | Cooling Capacity (kWatt) |  |  | 5.28 (2.90-5.74) | 7.03 (3.22-8.21) | 10.55 (4.04-12.02) | 14.07 (4.75-14.58) | 15.53 (5.28-16.71)
|  | Heating Capacity (Btu/h) |  |  | 18.500 (8.100-20.800) | 26.000 (8.300-29.500) | 38.000 (10.050-46.000) | 55.000 (13.396-57.206) | 62.000 (15.000-66.000)
|  | Heating Capacity (kWatt) |  |  | 5.42 (2.37-6.10) | 7.62 (2.43-8.65) | 11.14 (2.94-13.48) | 16.12 (3.93-16.77) | 18.17 (4.4-19.34)
|  | Seasonal Efficiency (In accordance to EN14825 | Cooling | Pdesign (kW) | 5.3 | 7.0 | 10.5 | 14.0 | 15.7
|  |  |  | Energy Class | A++ | A++ | A++ | A++ | A++
|  |  |  | SEER | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
|  |  | Heating (Middle Zone) | Pdesign (kW) | 4.2 | 5.4 | 8.8 | 11.2 | 11.9
|  |  |  | Energy Class | A+ | A+ | A+ | A+ | A+
|  |  |  | SCOP | 4.0 | 4.0 | 4.0 | 4.0 | 4.0
|  |  | Heating (Warm Zone) | Pdesign (kW) | 5.3 | 5.8 | 10.5 | 12.5 | 12.5
|  |  |  | Energy Class | A++ | A++ | A++ | A++ | A+++
|  |  |  | SCOP | 4.9 | 4.9 | 4.9 | 4.8 | 5.1
|  | Voltage/Frequency/Phase (V/Hz/Ph) |  |  | 220-240/50/1 | 220-240/50/1 | 220-240/50/1 | 380-415/50/3 | 380-415/50/3
|  | Current Input (A) |  | Cooling | 7.2 (3.2-8.2) | 9.5 (2.1-12.4) | 16.3 (3.9-19.6) | 8.3 (1.8-9.3) | 9.8 (1.8-11.6)
|  |  |  | Heating | 6.4 (3.1-8.5) | 8.9 (2.2-12.5) | 13.0 (3.2-19.4) | 8.2 (1.56-8.9) | 9.9 (1.6-11.2)
|  | Power Input (W) |  | Cooling | 1.633 (720-1.860) | 2.190 (480-2.850) | 3.750 (890-4.500) | 5.130 (1.174-5.602) | 5.951 (1.147-6.682)
|  |  |  | Heating | 1.460 (700-1.930) | 2.050 (500-2.880) | 2.993 (720-4.450) | 5.050 (987-5.378) | 6.036 (1.022-6.448)
|  | Air Flow Volume (High/Medium/Low) (m3/h) |  |  | 720/625/540 | 1.378/1.200/1.032 | 1.775/1.620/1.438 | 1.715/1.568/1.381 | 1.970/1.737/1.537
|  | Noise Level [dB(A)] |  | Indoor unit (Low/Medium/High) | 35.5/39/42.5 | 40/43/47 | 46/49/51 | 49/50/52 | 48/50.5/53
|  |  |  | Outdoor unit | 55 | 62 | 65 | 66 | 66
|  | Sound Power Level [dB(A)] |  | Indoor/Outdoor Unit | 56/63 | 59/64 | 61/66 | 65/72 | 62/65
|  | Power Supply Wire Outdoor / Fuses (Νοxmm2)/(Α) |  |  | 3x2.5 / 1x16 | 3x2.5 / 1x16 | 3x4.0 / 1x25 | 5x2.5 / 3x20 | 5x2.5 / 3x20
|  | Power Supply Wire Indoor / Fuses (Νοxmm2)/(Α) |  |  | - | 3x1.5 / 1x10 | 3x1.5 / 1x10 | 3x1.5 / 1x10 | 3x1.5 / 1x10
|  | Signal Wires (Noxmm2) |  |  | 4 x 1.5 | 2 × 1.0 Shield | 2 × 1.0 Shield | 2 × 1.0 Shield | 2 × 1.0 Shield
|  | Dimensions (WxDxH) (mm) |  | Panel | 647x647x50 | 950x950x55 | 950x950x55 | 950x950x55 | 950x950x55
|  |  |  | Indoor Unit | 570x570x260 | 840x840x245 | 840x840x245 | 840x840x287 | 840x840x287
|  |  |  | Outdoor Unit | 800x333x554 | 845x363x702 | 946x410x810 | 952x415x1.333 | 952x415x1.333
|  | Net Weight (kg) |  | Panel/Indoor/Outdoor Unit | 2.5/16.2/33.7 | 5.0/23.0/49.4 | 5.0/27.5/66.8 | 5.0/29.0/106.7 | 5.0/29.7/111.3
|  | Liquid Line ¦Gas Line |  |  | 1/4" ¦ 1/2" | 3/8" ¦ 5/8" | 3/8" ¦ 5/8" | 3/8" ¦ 5/8" | 3/8" ¦ 5/8"
|  | Refrigerant/Charge (g) |  |  | R32/1.150 | R32/1.500 | R32/2.400 | R32/2.800 | R32/2.950
|  | Operation Temperature Range (°C) Cooling/Heating |  |  | -15~50/-15~24 | -15~50/-15~24 | -15~50/-15~24 | -15~50/-15~24 | -15~50/-15~24
FEATURES | MAIN USP | 360° Air Outlet
| 2nd USP | Hotel Menu
| 3rd USP | External Air Duct Outlet
| 4th USP | Wi-Fi Ready
| 5th USP | Anti-Cold Air Function
| other features | Built-in Drain Pump
Fresh Air Intake
Golden Fin
Central Control Management (Optional)
A++ Energy Class
Front Desk Control On/Off (Optional)
Error Alarm Port
Fan On/Off Switch
Temperature Sensor Offset
Low Ambient Cooling
Excellent Heating Performance Under -15°C
Quiet Operation
Smart Controller
24-Hours Timer
Error Alarm Port
Auto Restart
Auto Error Diagnosis
All DC Inverter