## LCAC_V7_Cassettes_EN
EN |  |  |  |  | MODEL NAMES
[5 empty] | V7CRI-12WiFiR / U7RS-12 | V7CRI-18WiFiR / U7RS-18 | V7CI-24WiFiR / U7RS-24 | V7CI-36WiFiR / U7RS-36 | V7CI-42WiFiR / U7RS-42 | V7CI-50WiFiR / U7RT-50 | V7CI-60WiFiR / U7RT-60
SPECIFICATIONS |  | Cooling Capacity (Btu/h) |  |  | 12.000 (2.897~14.020) | 18.000 (9.900~19.064) | 24.000 (11.263~27.000) | 36.000 (9.200~39.000) | 41.000 (10.000~42.000) | 48.000 (12.000~54.000) | 53.000 (14.000~57.000)
|  | Cooling Capacity (kWatt) |  |  | 3.52 (0.85~4.11) | 5.28 (2.90~5.59） | 7.03 (3.30~7.91） | 10.55 (2.70~11.43） | 12.02 (2.93~12.31) | 14.07 (3.52~15.83) | 15.24 (4.10~16.71)
|  | Heating Capacity (Btu/h) |  |  | 13.000 (1.604~14.705) | 19.000 (8.100~20.800) | 26.000 (9.577~30.500) | 38.000 (9.500~42.000) | 46.000 (11.500~48.000) | 55.000 (14.000~59.000) | 62.000 (15.000~68.000)
|  | Heating Capacity (kWatt) |  |  | 3.81(0.47~4.31) | 5.57 (2.37~6.10) | 7.62 (2.81~8.94) | 11.14 (2.78~12.30) | 13.48 (3.37~14.07) | 16.12 (4.10~17.29) | 18.17 (4.40~19.93)
|  | Seasonal Efficiency (In accordance to EN14825 | Cooling | Pdesign (kW) | 3.5 | 5.3 | 7.0 | 10.5 | 12.1 | 14.0 | 15.3
|  |  |  | Energy Class | A++ | A++ | A++ | A++ | A++ | A++ | A++
|  |  |  | SEER | 6.6 | 6.3 | 6.2 | 6.7 | 6.1 | 6.1 | 6.3
|  |  | Heating (Middle Zone) | Pdesign (kW) | 2.7 | 4.2 | 6.0 | 8.5 | 9.5 | 11.0 | 11.9
|  |  |  | Energy Class | A+ | A+ | A+ | A+ | A+ | A+ | A+
|  |  |  | SCOP | 4.1 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0
|  |  | Heating (Warm Zone) | Pdesign (kW) | 3.3 | 5.4 | 6.3 | 10.1 | 9.8 | 12.0 | 12.5
|  |  |  | Energy Class | A+++ | A++ | A+++ | A+++ | A+++ | A++ | A+++
|  |  |  | SCOP | 5.1 | 4.8 | 5.1 | 5.1 | 5.1 | 5.0 | 5.1
|  | Voltage/Frequency/Phase (V/Hz/Ph) |  |  | 220-240/50/1 | 220-240/50/1 | 220-240/50/1 | 220-240/50/1 | 220-240/50/1 | 380-415/50/3 | 380-415/50/3
|  | Current Input (A) |  | Cooling | 4.45 (1.32-6.31) | 7.20 (3.20-9.20) | 10.20 (4.20-12.00) | 17.50 (4.20-18.50) | 18.80 (3.10-19.10) | 8.10 (1.80-10.20) | 8.60 (2.10-10.70)
|  |  |  | Heating | 4.73 (1.04-6.07) | 6.80 (3.10-8.50) | 8.50 (3.60-12.10) | 13.50 (3.50-17.50) | 16.30 (3.40-19.00) | 8.00 (1.90-9.50) | 9.60 (2.10-10.70)
|  | Power Input (kW) |  | Cooling | 1.01 (0.17-1.43) | 1.63 (0.72-2.09) | 2.32 (0.78-2.75) | 3.95 (0.90-4.20) | 4.20 (0.68-4.35) | 4.65 (0.80-5.90) | 5.00 (0.98-6.20)
|  |  |  | Heating | 1.02 (0.12-1.38) | 1.54 (0.70-1.93) | 1.90 (0.61-2.70) | 3.70 (0.75-4.25) | 3.70 (0.75-4.25) | 4.58 (0.90-5.50) | 5.55 (1.2-6.70)
|  | Air Flow Volume (High/Medium/Low) (m3/h) |  |  | 620/510/420 | 720/620/500 | 1.300/1.140/1.000 | 1.700/1.550/1.380 | 1.900/1.750/1.600 | 1.970/1.780/1.580 | 2.000/1.850/1.650
|  | Noise Level [dB(A)] |  | Indoor unit (Low/Medium/High) | 25.5/33/36/41 | 29/35.5/39.5/43 | 27/39.5/42.5/45.5 | 39/44.5/47.5/50 | 38/46/48.5/51 | 37.5/46.5/48.5/51 | 40/48/50.5/53
|  |  |  | Outdoor unit | 53.6 | 56 | 60 | 63 | 63 | 63.5 | 64
|  | Sound Power Level [dB(A)] |  | Indoor/Outdoor Unit | 56/60 | 57/63 | 57/67 | 63/70 | 65/71 | 65/73 | 65/73
|  | Power Supply Wire Outdoor / Fuses (Νοxmm2)/(Α) |  |  | 3x1.5 / 1x10 | 3x2.5 / 1x16 | 3x2.5 / 16 | 3x4.0 / 1x25 | 3x4.0 / 1x25 | 5x2.5 / 3x16 | 5x2.5 / 3x16
|  | Signal Wires (Noxmm2) |  |  | 4x1.5 | 4x1.5 | 4x1.5 | 4x1.5 | 4x1.5 | 4x1.5 | 4x1.5
|  | Dimensions (WxDxH) (mm) |  | Panel | 647x647x50 | 647x647x50 | 950x950x55 | 950x950x55 | 950x950x55 | 950x950x55 | 950x950x55
|  |  |  | Indoor Unit | 570x570x260 | 570x570x260 | 830x830x205 | 830x830x245 | 830x830x287 | 830x830x287 | 830x830x287
|  |  |  | Outdoor Unit | 765x303x555 | 805x330x554 | 890x342x673 | 946x410x810 | 946x410x810 | 952x415x1.333 | 952x415x1.333
|  | Net Weight (kg) |  | Panel/Indoor/Outdoor Unit | 2.5/16.3/26.6 | 2.5/16.0/32.5 | 6.0/21.6/43.9 | 6.0/27.2/66.9 | 6.0/29.3/71.0 | 6.0/29.3/103.7 | 6.0/29.3/107.0
|  | Liquid Line ¦Gas Line |  |  | 1/4" ¦ 3/8" | 1/4" ¦ 1/2" | 3/8" ¦ 5/8" | 3/8" ¦ 5/8" | 3/8" ¦ 5/8" | 3/8" ¦ 5/8" | 3/8" ¦ 5/8"
|  | Refrigerant/Charge (g) |  |  | R32/720 | R32/1.150 | R32/1.500 | R32/2.400 | R32/2.800 | R32/2.900 | R32/3.000
|  | Operation Temperature Range (°C) Cooling/Heating |  |  | -15～50 / -15～24 | -15～50 / -15～24 | -15～50 / -15～24 | -15～50 / -15～24 | -15～50 / -15～24 | -15～50 / -15～24 | -15～50 / -15～24
FEATURES | MAIN USP | 360° Air Outlet
| 2nd USP | Independent Louver Swing* (units 24.000~60.000btu/h)
| 3rd USP | Hotel Menu
| 4th USP | Wi-Fi Ready
| 5th USP | Fresh Air Intake
| other features | Built-in Drain Pump
External Air Duct Outlet
Central Control Management (Optional)
Weekly Planner Controller (optional)
Golden Fin
Follow Me
A++ Energy Class
Front Desk Control On/Off
Smart Controller
ECO Mode
GEAR Mode
iClean Mode
24-Hours Timer
Quiet Operation
Sleep Mode
Turbo Mode
Weekly Program Delay (Optional with the Weekly Planner Controller)
Operation Mode Lock (Optional with the Weekly Planner Controller)
Remote Controller Commands Deactivation (Optional with the Weekly Planner Controller)
Temperature Sensor Offset
Anti-Cold Air Function
Low Ambient Cooling
Excellent Heating Performance Under -15°C
Auto Error Diagnosis
Auto Restart
Refrigerant Leakage Detect
Mute Mode
Lock
All DC Inverter
R32 ECO Refrigerant